# Surge Arresters (Разрядники)
## Manufacturers
Bourns
TDK\EPCOS	https://www.tdk-electronics.tdk.com/en/arresters
Littelfuse
BrightKing
RUICHI
CITEL	http://www.tecnorayos.com/pdf/3.CAPSULAS%20GASEOSAS%20CITEL.pdf
DEHN
LEUTRON
OBO Bettermann
Phoenix Contact
RST
ГРОЗОЩИТ
ДКС
Тахион
KLS
ZF

https://skomplekt.com/tovar/6/27/12/
https://www.symmetron.ru/catalog/passivnye-komponenty/razryadniki/
## Theory
The main electrical characteristics defining a gas discharge tube are:
- DC sparkover voltage (Volts)
- Impulse sparkover voltage (Volts)
- Discharge current capacity (kA)
- Insulation resistance (Gohms)
- Capacitance (pF)

### DC sparkover voltage
This is the main characteristic defining the gas discharge tube. It is the voltage at which breakdown will occur between the electrodes when a slowly increasing voltage (dV/dt = 100 V/s) is applied to the component; it depends on the electrode spacing, the pressure, and the properties of the gas mixture and of the emissive substance.
Range of DC sparkover voltages available:
- minimum 75V
- average 230V
- high voltage 500V
- very high voltage 1000 to 3000V
The tolerance on the breakdown voltage is generally ± 20%.
### 3-electrode configuration
Protecting a two-wire line (for example a telephone pair) with two 2- electrode gas discharge tubes (connected between the wires and ground) may cause the following problem:
The line is subjected to an overvoltage in common mode; because of the dispersion of the sparkover voltages (± 20%), one of the gas discharge tubes sparks over a very short time before the other (a few microseconds); the wire that has sparked over is therefore grounded (neglecting the arc voltages), turning the common-mode overvoltage into a differential-mode overvoltage, very dangerous for the terminal equipment. This risk disappears when the second gas discharge tube arcs over (a few microseconds later).
3-electrode geometry eliminates this drawback: the sparkover of one pole causes a «general» breakdown of the device almost instantaneously (a few nanoseconds) because there is only one gasfilled enclosure.
### End of life
Gas discharge tubes are designed to withstand several impulses without destruction or loss of the initial characteristics (typical impulse tests: 10 times 5kA impulses of each polarity).
On the other hand, a sustained strong current (e.g. 10A rms for 15 seconds, simulating the fall of a power line onto a telecommunications line) will put the device out of service definitively.
If a fail-safe end of life is desired (i.e. a short-circuit that will report the fault to the user when the line fault is detected), gas discharge tubes with the fail-safe feature (external short-circuit) should be chosen.
## Radial - TH
### 2-PIN

Mounting
### 3-PIN

## SMD
### 2-PIN

Bourns	2051-09-SM-RPLF		(4.5×3.2×2.7mm 90V +30% 2kA/2A), SMD 2.7×3.2×4.5mm 90V +30% 2kA/2A.
Epcos	M50-C90XSMD	B88069X1640T902	(5.4x5mm 90V +20% 10kA/5A 2-х элек. SMD M50-C90XSMD), 5.4x5mm 90V +20% 10kA/5A 2-х элек. SMD

### 3-PIN
## Cable\Connector
https://www.panorama-antennas.com/site/Antenna-Accessories/Surge-Arresters?product_id=380
## Disk - TH + varistor